## Slide 1: Embedded Networks Solar Emergency Backstop

## Slide 2
Contents
1. New requirements for solar PV in embedded networks
2. Scenarios – Greenfield site
  2a. Greenfield site. Fully CSIP-AUS enabled
  2b. Greenfield site. Partially CSIP-AUS enabled
3. Scenarios – Brownfield site
  3a. Brownfield site. New solar CSIP-AUS enabled
  3b. Brownfield site. New solar export limited
  3c. Brownfield site. New large solar CSIP-AUS enabled
  3d. Brownfield site. New large solar CSIP-AUS enabled
  3e. Brownfield site. New solar GMM controlled

## Slide 3
  New, upgraded or replaced solar PV generation within an embedded network must be emergency backstop enabled, allowing the Distribution Network Service Provider (DNSP) to curtail or disconnect the generation when called upon by the Australian Energy Market Operator (AEMO)
  The emergency backstop capability can be achieved using:
  CSIP-AUS control of the inverter
  Generator Monitor Meters
  Where the Embedded Network Operator (ENO) cannot practicably apply the emergency backstop capability to solar systems within the Embedded Network (EN), the ENO must ensure that each individual solar PV system which cannot practically connect are export limited to 0kW
  Legacy solar PV systems within an embedded network will be backstop exempt
  Standalone or AC coupled Battery Energy Storage Systems (BESS) will also be backstop exempt
New requirements for Solar PV in embedded networks

## Slide 4: Greenfield site Fully CSIP-AUS enabled
A greenfield EN site with individual dwelling solar systems, large common area solar and battery energy storage systems (BESS)
All solar generation in the EN is emergency backstop enabled via CSIP-AUS commands from the DNSP. The ENO implements a single site generation control system to interface with the DNSP
BESS is emergency backstop exempt
Scenario 2a

## Slide 5: Greenfield site Partially CSIP-AUS enabled
A greenfield EN site with individual dwelling solar systems, large common area solar and Battery Energy Storage Systems (BESS)
Large solar generation in the EN is emergency backstop enabled via CSIP-AUS commands from the DNSP. The ENO implements a single site generation control system to interface with the DNSP
Individual solar cannot practicably connect to the controls system and is export limited at the individual site with export metering (M2) installed for each location
BESS is emergency backstop exempt
Scenario 2b

## Slide 6: Brownfield site New Solar CSIP-AUS enabled
A brownfield EN site with individual dwelling solar systems, large common area solar and battery energy storage systems (BESS)
All new solar generation in the EN is emergency backstop enabled via CSIP-AUS commands from the DNSP. The ENO implements a single site generation control system to interface with the DNSP
Commissioning of the new site generation control capability will need to be performed manually and take into account existing solar generation. Site export limit zero commands will ramp down all controlled generation to zero if the legacy solar is generating and the site is exporting
The legacy solar remains emergency backstop exempt
BESS is emergency backstop exempt
Scenario 3a

## Slide 7: Brownfield site New Solar export limited
A brownfield EN site with individual dwelling solar systems, large common area solar and battery energy storage systems (BESS)
New solar generation cannot practicably be connected to a common control system. Each new system is export limited
ENO to provide confirmation that the newly installed solar is export limited at the individual site, with export metering (M2) installed for each location
The legacy solar remains emergency backstop exempt
BESS is emergency backstop exempt
Scenario 3b

## Slide 8: Brownfield site New large solar CSIP-AUS enabled
A brownfield EN site with existing individual dwelling solar systems
The new or upgraded large solar generation in the EN is Emergency Backstop enabled via CSIP-AUS commands from the DNSP. The ENO implements a single site generation control system to interface with the DNSP
Commissioning of the new site generation control capability will need to be performed manually and consider existing solar generation. Site export limit zero commands will ramp down all controlled generation to zero if the legacy solar is generating and the site is exporting
The legacy solar remains emergency backstop exempt
BESS is emergency backstop exempt
Scenario 3c

## Slide 9: Brownfield site New large solar CSIP-AUS enabled
A brownfield EN site with existing individual dwelling solar systems
The new or upgraded large solar generation in the EN is Emergency Backstop enabled via CSIP-AUS commands from the DNSP. The ENO implements a single site generation control system to interface with the DNSP
Commissioning of the new site generation control capability will need to be performed manually and consider existing solar generation. Site export limit zero commands will ramp down all controlled generation to zero if the legacy solar is generating and the site is exporting
The legacy solar remains emergency backstop exempt
Scenario 3d

## Slide 10: Brownfield site New large solar GMM controlled
A brownfield EN site with existing individual dwelling solar systems
The new large solar generation in the EN is emergency backstop enabled via the Generator Monitor Meter (GMM) solution
Emergency backstop control signals trip the generator CB.
The legacy solar remains emergency backstop exempt
BESS is emergency backstop exempt
Scenario 3e